## Slide 1: Quick Look KPP#1: Load Outage Duration
Vendor #1 | Critical | Priority | Interruptible
% KWh Outage | 57% | 88% | 85%
% Time Outage | 55% | 88% | 83%
Vendor #2 |  |  | 
% KWh Outage | 50% | 91% | 91%
% Time Outage | 48% | 91% | 91%

## Slide 2: Quick Look KPP #2: Energy Cost
CHP thermal plant was not being actively controlled,
not sure why boiler emissions were different

## Slide 3: Quick Look KPP#3: Fuel Consumption During Islanded Condition
 | Diesel (gpm) | CHP (Nm3/min) | Boiler (Nm3/min)
Vendor #1 | 0.86 | 7.6 | 7.5
Vendor #2 | 1.1 | 8.7 | 11.3
CHP thermal plant was not being actively controlled,
not sure why boiler emissions were different