## PacketFormat
| Update Rate (Hz) | 5
Scaling
Header | Name | DataType | Points | Qty | Total B/s | Gain | Units - Notes
| Start byte | int16 | 1 | 1 | 10 |  | 0xAFAF
Waveform Data | Waveform | int16 | 1 | 3 | 30 | 1 | Vpu
Relay Data | Power Real | int16 | 1 | 20 | 200 | 10 | kw
Relay Data | Power Reactive | int16 | 1 | 20 | 200 | 10 | kvar
Relay Data | Voltage | int16 | 1 | 20 | 200 | 100 | Vpu
Relay Data | Frequency | int16 | 1 | 20 | 200 | 100 | Hz
Relay Data | Breaker Status | int16 | 1 | 20 | 200 | 1 | may change to Bit field - 8bits per breaker
BESS Data | BESS Data | int16 | 1 | 1 | 10 | 1 | N/A
Diesel Gensets data | Fuel comsumption | int16 | 1 | 1 | 10 | 100 | gals/hr
Diesel Gensets data | Terminal voltage diesel | int16 | 1 | 1 | 10 | 100 | Vpu
NGCHP Gensets data | Terminal voltage NGCHP | int16 | 1 | 1 | 10 | 100 | Vpu
NGCHP Gensets data | Temp Actual | int16 | 1 | 1 | 10 | 100 | degrees C
NGCHP Gensets data | Heat Recovered | int16 | 1 | 1 | 10 | 100 | Mbtu/hr
NGCHP Gensets data | Fuel usage | int16 | 1 | 1 | 10 | 100 | Nm^3/hr
NGCHP Gensets data | CHP CO2 | int16 | 1 | 1 | 10 | 100 | lbm/hr
NGCHP Gensets data | Heat from boiler | int16 | 1 | 1 | 10 | 100 | Mbtu/hr
NGCHP Gensets data | CHP heat contribution | int16 | 1 | 1 | 10 | 100 | Mbtu/hr
NGCHP Gensets data | Boiler Nm^3/hr | int16 | 1 | 1 | 10 | 100 | Nm^3/hr
NGCHP Gensets data | Boiler lbm/hr CO2 | int16 | 1 | 1 | 10 | 100 | lbm/hr
Motor data | F1 Motor Status | int16 | 1 | 1 | 10 | 1 | on/off state
PV data | PV data | int16 | 1 | 1 | 10 | 1 | N/A
Power Factor Data | Power Factor | int16 | 1 | 1 | 10 | 1000 | N/A
Power Factor Data | Import/Export | int16 | 1 | 1 | 10 | 1 | 1:import/0:export
Power Factor Data | Lagging/Leading | int16 | 1 | 1 | 10 | 1 | 1:lagging/0:leading
Misc Data | Misc Data | int16 | 1 | 3 | 30 | 1 | N/A
| Stop byte | int16 | 1 | 1 | 10 |  | 0x5555
| Checksum | int16 | 1 | 1 | 10 |  | Add all the bytes with overflow. Send bottom 16-bits
126
|  |  |  | Total Data Rate (B/s) | 1260