## SEL2440
I/O Point | Description | Bit
OUT101 | I1 load shed (CB104) | 1=shed
OUT102 | I2 load shed (CB107) | 1=shed
OUT103 | I3 load shed (CB206) | 1=shed
OUT104 | I4 load shed (CB208) | 1=shed
OUT105 | I5 load shed (CB212) | 1=shed
OUT106 | I6 load shed (CB308) | 1=shed
OUT107 | P1 load shed (CB114) | 1=shed
OUT108 | P2 load shed (CB219) | 1=shed
OUT109 | P3 load shed (CB204) | 1=shed
OUT110 | P4 load shed (CB307) | 1=shed
OUT111 | P5 load shed (CB218) | 1=shed
OUT112 | P6 load shed (CB309) | 1=shed
OUT113
OUT114
OUT115
OUT116
IN201 | I1 load status (CB104) | 1=closed
IN202 | I2 load status (CB107) | 1=closed
IN203 | I3 load status (CB206) | 1=closed
IN204 | I4 load status (CB208) | 1=closed
IN205 | I5 load status (CB212) | 1=closed
IN206 | I6 load status (CB308) | 1=closed
IN207 | P1 load status (CB114) | 1=closed
IN208 | P2 load status (CB219) | 1=closed
IN209 | P3 load status (CB204) | 1=closed
IN210 | P4 load status (CB307) | 1=closed
IN211 | P5 load status (CB218) | 1=closed
IN212 | P6 load status (CB309) | 1=closed
IN213 | Diesel Gen breaker status (F1-GCB) | 1=closed
IN214 | BESS breaker status (CB205) | 1=closed
IN215 | PV breaker status (CB211) | 1=closed
IN216 | CHP Gen breaker Status (F3-GCB) | 1=closed
IN301 | 751-1 | 1=closed
IN302 | 751-2 | 1=closed
IN303 | 751-3 | 1=closed
IN304 | CB101 | 1=closed
IN305 | CB102 | 1=closed
IN306 | CB103 | 1=closed
IN307 | CB108 | 1=closed
IN308 | CB201 | 1=closed
IN309 | CB202 | 1=closed
IN310 | CB203 | 1=closed
IN311 | CB301 | 1=closed
IN312 | CB302 | 1=closed
IN313 | CB303 | 1=closed
IN314 | CB304 | 1=closed
IN315 | spare
IN316 | DC whetting | 1=OK