## UDPPacket_info
| Update Rate (Hz) | 5
Scaling
Header | Name | DataType | Points | Qty | Total B/s |  | Gain | Offset | Units
| Start byte | int16 | 1 | 1 | 10 |  |  |  | 0xAFAF
Waveform Data | Waveform | int16 | 166 | 3 | 4980 |  | 100 |  | pu
Relay Data | Power Real | int16 | 1 | 4 | 40 |  | 10 |  | kw
Relay Data | Power Reactive | int16 | 1 | 4 | 40 |  | 10 |  | kvar
Relay Data | Voltage | int16 | 1 | 4 | 40 |  | 100 |  | pu
Relay Data | Frequency | int16 | 1 | 4 | 40 |  | 100 |  | Hz
Relay Data | Breaker Status | int16 | 1 | 4 | 40 |  |  |  | Bit field - 8bits per breaker
BESS Data | BESS Data | int16 | 1 | 0 | 0
Generator data | Generator data | int16 | 1 | 0 | 0
Motor data | on/off state | int16 | 1 | 1 | 10 |  |  |  | on/off
PV data | PV data | int16 | 1 | 0 | 0
Misc Data | Misc Data Set#1 | int16 | 1 | 1 | 10 |  | 1000 |  | PF
| Misc Data Set#2 | int17 | 1 | 6 | 63.75 |  | 100 |  | VRMSLL, Hz, degrees-angle
Misc Data | Misc Data Set#3 | int16 | 1 | 3 | 30 |  | 10 |  | Btu/Hr, and degree F
| Stop byte | int16 | 1 | 1 | 10 |  |  |  | 0x5555
| Checksum | int16 | 1 | 1 | 10 |  |  |  | Add all the bytes with overflow. Send bottom 16-bits
532
|  |  | Total Data Rate (B/s) |  | 5323.75
| Num of breaker to display | 4
| Breaker Positions |  | Frequency |  | Breaker Status (LSB on right)
| 1 | MID | CB2 |  | 1 | 2-1
| 2 | GCB | CB3 |  | 2 | 4-3
| 3 | CB2
| 4 | CB3