## relays
Relay# | VRMSLL | Max. Slip Voltage [%] | Max. Slip Angle [degree] | Max. Slip Frequency [Hz] | 27P and 59P Trip Delay [Sec] | CT Primary : 5 | CB Initial State [closed=1; open=0] | 50P IOC Trip Pickup [Amp. Sec] | 50P IOC Trip Delay [Sec] | 51P TOC Trip Pickup [Amp. Sec] | 51P Curve Type | 51P TOC Time Dial | 27P Trip Pickup [pu] | 59P Trip Pickup [pu] | 81U Trip Pickup [Hz] | 81U Trip Delay [Sec] | 81O Trip Pickup [Hz] | 81O Trip Delay [Sec] | 81RFRP [Hz/Sec] | 81RFDFP [Hz] | 81RF Trip Delay [Sec] | 50P IOC Trip Pickup [Amp. Sec] | 50P IOC Trip Delay [Sec] | 51P TOC Trip Pickup [Amp. Sec] | 51P Curve Type | 51P TOC Time Dial | 27P Trip Pickup [pu] | 59P Trip Pickup [pu] | 81U Trip Pickup [Hz] | 81U Trip Delay [Sec] | 81O Trip Pickup [Hz] | 81O Trip Delay [Sec] | 81RFRP [Hz/Sec] | 81RFDFP [Hz] | 81RF Trip Delay [Sec]
1 | 13800 | 5 | 12 | 0.5 | 2 | 1200 | 0 | 20 | 0 | 0.60141 | 1 | 1 | 0.7 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01 | 20 | 0 | 0.60141 | 1 | 1 | 0.5 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01
2 | 480 | 10 | 12 | 0.5 | 2 | 3500 | 0 | 20 | 0 | 1 | 1 | 1 | 0.7 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01 | 20 | 0 | 0.40094 | 1 | 1 | 0.5 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01
3 | 480 | 10 | 12 | 0.5 | 2 | 3500 | 0 | 20 | 0 | 2 | 1 | 1 | 0.7 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01 | 20 | 0 | 0.40094 | 1 | 1 | 0.5 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01
4 | 13800 | 5 | 12 | 0.5 | 2 | 1200 | 0 | 20 | 0 | 0.60141 | 1 | 1 | 0.7 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01 | 20 | 0 | 0.60141 | 1 | 1 | 0.5 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01
5 | 480 | 10 | 12 | 0.5 | 2 | 3500 | 0 | 20 | 0 | 0.40094 | 1 | 1 | 0.7 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01 | 20 | 0 | 0.40094 | 1 | 1 | 0.5 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01
6 | 480 | 10 | 12 | 0.5 | 2 | 3500 | 0 | 20 | 0 | 0.40094 | 1 | 1 | 0.7 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01 | 20 | 0 | 0.40094 | 1 | 1 | 0.5 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01
7 | 480 | 10 | 12 | 0.5 | 2 | 3500 | 0 | 20 | 0 | 1.1856 | 1 | 1 | 0.7 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01 | 20 | 0 | 1.1856 | 1 | 1 | 0.5 | 1.2 | 54 | 2 | 66 | 2 | 2 | 57 | 0.01
% Copyright (c) 2016 Massachusetts Institute of Technology
% Permission is hereby granted, free of charge, to any person obtaining a copy of this
% software and associated documentation files (the "Software"), to deal in the Software
% without restriction, including without limitation the rights to use, copy, modify,
% merge, publish, distribute, sublicense, and/or sell copies of the Software, and to
% permit persons to whom the Software is furnished to do so, subject to the following
% conditions:
%
%
% The above copyright notice and this permission notice shall be included in
% all copies or substantial portions of the Software.
%
% THE SOFTWARE IS PROVIDED "AS IS", WITHOUT WARRANTY OF ANY KIND, EXPRESS OR IMPLIED,
% INCLUDING BUT NOT LIMITED TO THE WARRANTIES OF MERCHANTABILITY, FITNESS FOR A
% PARTICULAR PURPOSE AND NONINFRINGEMENT. IN NO EVENT SHALL THE AUTHORS OR COPYRIGHT
% HOLDERS BE LIABLE FOR ANY CLAIM, DAMAGES OR OTHER LIABILITY, WHETHER IN AN ACTION
% OF CONTRACT, TORT OR OTHERWISE, ARISING FROM, OUT OF OR IN CONNECTION WITH THE
% SOFTWARE OR THE USE OR OTHER DEALINGS IN THE SOFTWARE.
%
%
NOTES:
51P Curve:
1: moderate inverse
2: inverse
3: very inverse
4: extremely inverse