## Sheet1
Modbus Item (IP Address : Port) | Variable | Register Address (Might need to add "1") | Modbus Register Type | Modbus Data Type | Units | Range | Notes
CHP (192.168.10.30 : 1050) | Temp, Actual | 0 | Input Register | Single Integer | deg F | 0-215
| CHP Heat Supplied | 1 | Input Register | Single Integer | Mbtu/hr | 0-215
| Boiler Heat Supplied | 2 | Input Register | Single Integer | Mbtu/hr | 0-215
| NG Usage | 3 | Input Register | Single Integer | Nm3/hr | 0-215
| CO2 | 4 | Input Register | Single Integer | lbm/hr | 0-215
| Temp Set Point | 2000 | Holding Register | Single Integer | deg F | 0-215
| CHP Enable/Disable | 2001 | Holding Register | Single Integer | 1=Enable; 0=Disable | 0,1
NG easYgen 3500 (192.168.10.35 : 502) | Remote F setpoint | 509 | Holding Register | Integer | Hz ("60000"=60 Hz) | 0-7000
| Remote V setpoint | 510 | Holding Register | Long Integer | VRMS ("13800"=13800 VRMS) | 50-650000
| P setpoint | 5520 | Holding Register | Long Integer | kW ("15000"=1.5MW) | 0-999999
| PF setpoint | 508 | Holding Register | Decimal | Per Unit | -710-1000-710
| Auto/Stop;F Droop On/Off; V Droop On/Off | 505 | Holding Register | Binary | xxxxxxxxxxxxxxx0 = Stop Mode xxxxxxxxxxxxxxx1 = Auto Mode xxxxxxxxxxxxx1xx = F Droop On xxxxxxxxxxxxx0xx = F Droop Off 1xxxxxxxxxxxxxxx = V Droop On 0xxxxxxxxxxxxxxx = V Droop Off | 0,1
SEL751 Relay F1 (192.168.10.51 : 502) | Initiate Synch (Positive Edge Triggered) | 27 | COIL | - | 01h=Read COIL Status 05h=Force Single Coil | 01h, 05h
| Open F1 | 28 | COIL | - | 01h=Read COIL Status 05h=Force Single Coil | 01h, 05h | Not yet implemented as of 10/14/2016