## v1
Time | Test Condition | Initial Conditions | [19 empty] | Expected
|  | PCC #1-2-3 | Diesel | Solar Irradiance | Battery SoC | CHP | Load | Weather Forecast | Temperature (degF) | Motor #1-2 | Fault | Nat. Gas Fuel Price ($/gal) | Diesel Fuel Cost ($/gal) | ISONE Spot Price ($/MWh) | DSO Command/Request | DSO Import/Export Value (kW) | DSO Power Factor Value | DSO Var Support Value (kVAR) | DSO Demand Response Value (kW) | DSO Command Start Time | DSO Command Duration (min)
time |  | POI | diesel_breaker | pv_breaker |  | CHP_breaker | load_gain |  |  | motor | fault |  |  |  | dsoCommand | dsoImportExportValue | dsoPFValue | dsoVarValue | dsoDRValue | dsoCommandStartTime | dsoCommandDuration
0:00 | Steady state | C - C - C | ON | 60 | FULL | ON | 75 | N/A | 70 | OFF - ON | N/A | 2.5 | 2.4 | 23.3 | None | None | None | None | None | N/A | N/A
0:00 | Lose diesel | C - C - C | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 70 | OFF - ON | N/A | 2.5 | 2.4 | 23.3 | None | None | None | None | None | N/A | N/A | Increase import
0:00 | None, SS | C - C - C | OFF | 60 | ON (SoC as is) | ON | 75 | N/A | 71 | OFF - ON | N/A | 2.5 | 2.4 | 23.3 | None | None | None | None | None | N/A | N/A
0:00 | Increase load to hit import limit | C - C - C | OFF | 30 | ON (SoC as is) | ON | 100 | N/A | 71 | OFF - ON | N/A | 2.5 | 2.4 | 23.3 | Export | 1000 | None | None | None | 0:30 | 0:20 | Load shed
0:00 | None, SS | C - C - C | OFF | 30 | ON (SoC as is) | ON | 100 | N/A | 72 | OFF - ON | N/A | 2.5 | 2.4 | 25.08 | None | None | None | None | None | N/A | N/A | Restore load
0:00 | Restore diesel | C - C - C | ON | 30 | ON (SoC as is) | ON | 100 | N/A | 72 | OFF - ON | N/A | 2.5 | 2.4 | 25.08 | None | None | None | None | None | N/A | N/A
0:00 | Comply with export | C - C - C | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 73 | OFF - ON | N/A | 2.5 | 2.4 | 25.08 | None | None | None | None | None | N/A | N/A | Increase generation and ESS usage, load shed if nec.
0:00 | Lose PV | C - C - C | ON | OFF | ON (SoC as is) | ON | 75 | N/A | 73 | OFF - ON | N/A | 2.5 | 2.4 | 26.01 | None | None | None | None | None | N/A | N/A
0:00 | Fault on neighbor bus outside microgrid | C - C - C | ON | OFF | ON (SoC as is) | ON | 75 | N/A | 74 | OFF - ON | 8 | 2.5 | 2.4 | 26.01 | None | None | None | None | None | N/A | N/A | Increase diesel or load shed
0:00 | Restore PV | C - C - C | ON | 60 | ON (SoC as is) | ON | 50 | N/A | 74 | OFF - ON | N/A | 2.5 | 2.4 | 26.56 | Disconnect | None | None | None | None | 1:00 | N/A
0:00 | Fault within microgrid | C - C - C | ON | 60 | ON (SoC as is) | ON | 50 | N/A | 75 | OFF - ON | 1 | 2.5 | 2.4 | 26.56 | None | None | None | None | None | N/A | N/A | Reduce diesel or restore load
0:00 | DSO request disconnection at 1:00 | C - C - C | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 75 | OFF - ON | N/A | 2.5 | 2.4 | 27.46 | None | None | None | None | None | N/A | N/A
0:00 | Disconnection | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 76 | OFF - ON | N/A | 2.5 | 2.4 | 24.13 | None | None | None | None | None | N/A | N/A | MGC balances load and gen, disconnects
0:00 | Increase load to initial load shed scheme | O - O - O | ON | 30 | ON (SoC as is) | ON | 100 | N/A | 76 | OFF - ON | N/A | 2.5 | 2.4 | 24.13 | None | None | None | None | None | N/A | N/A
0:00 | return to normal load, loss of diesel gen | O - O - O | OFF | 100 | ON (SoC as is) | ON | 75 | N/A | 77 | OFF - ON | N/A | 2.5 | 2.4 | 26.01 | None | None | None | None | None | N/A | N/A
0:00 | short circuit fault within microgrid | O - O - O | OFF | 100 | ON (SoC as is) | ON | 75 | N/A | 78 | OFF - ON | 2 | 2.5 | 2.4 | 27.42 | None | None | None | None | None | N/A | N/A | Match generation and load
0:00 | restore diesel | O - O - O | ON | 100 | ON (SoC as is) | ON | 75 | N/A | 78 | OFF - ON | N/A | 2.5 | 2.4 | 27.46 | None | None | None | None | None | N/A | N/A
0:00 | Motor #1 start up | O - O - O | ON | 100 | ON (SoC as is) | ON | 75 | N/A | 79 | ON - ON | N/A | 2.5 | 2.4 | 27.46 | None | None | None | None | None | N/A | N/A
0:00 | Decrease load below available renewable | O - O - O | ON | 100 | ON (SoC as is) | ON | 50 | N/A | 80 | ON - ON | N/A | 2.5 | 2.4 | 32.7 | None | None | None | None | None | N/A | N/A | Load shed
0:00 | None, SS | O - O - O | ON | 60 | ON (SoC as is) | ON | 50 | N/A | 81 | ON - ON | N/A | 2.5 | 2.4 | 32.7 | None | None | None | None | None | N/A | N/A
0:00 | Normal load level | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 81 | ON - ON | N/A | 2.5 | 2.4 | 41.12 | None | None | None | None | None | N/A | N/A | Charge ESS or renewable spillage
0:00 | DSO request to reconnect at 2:00 | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 82 | ON - ON | N/A | 2.5 | 2.4 | 37.81 | Reconnect, power factor | None | None | None | None | 2:00 | 0:15
0:00 | Lose Motor #2 | O - O - O | ON | 60 | ON (SoC as is) | ON | 100 | N/A | 83 | ON - OFF | N/A | 2.5 | 2.4 | 37.83 | None | None | None | None | None | N/A | N/A | Return to grid-connected mode
0:00 | fill out | O - O - O | ON | 100 | ON (SoC as is) | ON | 100 | N/A | 84 | ON - OFF | N/A | 2.5 | 2.4 | 42.12 | None | None | None | None | None | N/A | N/A
0:00 | DSO pf command from 2:00 to 2:15 | C - C - C | ON | 100 | ON (SoC as is) | ON | 75 | N/A | 85 | ON - OFF | N/A | 2.5 | 2.4 | 42.12 | VAR | None | 0.99 | None | None | 2:15 | 0:15 | MGC increased VAR output of DERs
0:00 | Load variations, large PV variationn | C - C - C | ON | 100 | ON (SoC as is) | ON | 100 | N/A | 84 | ON - OFF | N/A | 2.5 | 2.4 | 41.48 | None | None | 0.99 | None | None | N/A | N/A
0:00 | Temporary fault at one of the service feeders | C - C - C | ON | 30 | ON (SoC as is) | ON | 50 | N/A | 84 | ON - OFF | 4 | 2.5 | 2.4 | 64.78 | None | None | 0.99 | None | None | N/A | N/A
0:00 | DSO command for Q from 2:15 to 2:30 (or Demand Response) | C - C - C | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 83 | ON - OFF | N/A | 2.5 | 2.4 | 64.78 | Demand response | None | None | 500 | None | 2:30 | 0:15
0:00 | Motor #2 start up | C - C - C | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 83 | ON - ON | N/A | 2.5 | 2.4 | 40.02 | None | None | None | 500 | None | N/A | N/A
0:00 | None, SS | C - C - C | ON | 60 | ON (SoC as is) | ON | 100 | N/A | 82 | ON - ON | N/A | 2.5 | 2.4 | 40.02 | None | None | None | 500 | None | N/A | N/A
0:01 | DSO command for Demand response from 2:30 to 2:45 | C - C - C | ON | 60 | ON (SoC as is) | ON | 100 | N/A | 81 | ON - ON | N/A | 2.5 | 2.4 | 34.94 | None | None | None | None | 1000 | N/A | N/A
0:01 | Load variations, large PV variationn | C - C - C | ON | 100 | ON (SoC as is) | ON | 100 | N/A | 81 | ON - ON | N/A | 2.5 | 2.4 | 34.94 | None | None | None | None | 1000 | N/A | N/A
0:01 | Load variations, large PV variationn | C - C - C | ON | 30 | ON (SoC as is) | ON | 50 | N/A | 80 | ON - ON | N/A | 2.5 | 2.4 | 34.94 | None | None | None | None | 1000 | N/A | N/A
0:01 | Unplanned disconnection by manual breaker operation | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 79 | ON - ON | N/A | 2.5 | 2.4 | 34.94 | None | None | None | None | 1000 | N/A | N/A
0:01 | None, SS | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 79 | ON - ON | N/A | 2.5 | 2.4 | 34.94 | None | None | None | None | None | N/A | N/A
0:01 | Fault within microgrid | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 78 | ON - ON | 3 | 2.5 | 2.4 | 37.31 | None | None | None | None | None | N/A | N/A
0:01 | Lose Motor #1 | O - O - O | ON | 60 | ON (SoC as is) | ON | 100 | N/A | 78 | OFF - ON | N/A | 2.5 | 2.4 | 37.31 | None | None | None | None | None | N/A | N/A
0:01 | Fault within microgrid | O - O - O | ON | 100 | ON (SoC as is) | ON | 100 | N/A | 77 | OFF - ON | 5 | 2.5 | 2.4 | 37.31 | None | None | None | None | None | N/A | N/A
0:01 | None, SS | O - O - O | ON | 100 | ON (SoC as is) | ON | 75 | N/A | 76 | OFF - ON | N/A | 2.5 | 2.4 | 27.42 | None | None | None | None | None | N/A | N/A
0:01 | Motor #1 start up | O - O - O | ON | 60 | ON (SoC as is) | ON | 50 | N/A | 75 | ON - ON | N/A | 2.5 | 2.4 | 27.42 | None | None | None | None | None | N/A | N/A
0:01 | Reconnection request for 3:25 | O - O - O | ON | 60 | ON (SoC as is) | ON | 50 | N/A | 75 | ON - ON | N/A | 2.5 | 2.4 | 27.42 | Reconnect | None | None | None | None | 3:25 | N/A
0:01 | Reconnect | C - C - C | ON | 30 | ON (SoC as is) | ON | 75 | N/A | 74 | ON - ON | N/A | 2.5 | 2.4 | 51.53 | None | None | None | None | None | N/A | N/A
0:01 | None, SS | C - C - C | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 74 | ON - ON | N/A | 2.5 | 2.4 | 51.53 | None | None | None | None | None | N/A | N/A
0:01 | Loss of PV | C - C - C | ON | OFF | ON (SoC as is) | ON | 100 | N/A | 73 | ON - ON | N/A | 2.5 | 2.4 | 51.53 | None | None | None | None | None | N/A | N/A
0:01 | Upstream fault causing unplanned disconnect | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 73 | ON - ON | 7 | 2.5 | 2.4 | 51.53 | None | None | None | None | None | N/A | N/A
3:45 | How long can the microgrid survive | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 72 | ON - ON | N/A | 2.5 | 2.4 | 54.75 | None | None | None | None | None | N/A | N/A
3:50 | How long can the microgrid survive | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 72 | ON - ON | N/A | 2.5 | 2.4 | 54.75 | None | None | None | None | None | N/A | N/A
3:55 | How long can the microgrid survive | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 71 | ON - ON | N/A | 2.5 | 2.4 | 54.75 | None | None | None | None | None | N/A | N/A
4:00 | How long can the microgrid survive | O - O - O | ON | 60 | ON (SoC as is) | ON | 75 | N/A | 70 | ON - ON | N/A | 2.5 | 2.4 | 54.75 | None | None | None | None | None | N/A | N/A | Eventually all fuel will run out

## Matlab CMDs
Time | Model Name | Parameter to Change | Parameter Name | Value to Set | Comments
0:05 | BANSHEE_SYSTEM/TestCommands' | Trip diesel generator relay - from close breaker to open breaker | diesel_breaker | breaker open = 1
0:25 | BANSHEE_SYSTEM/TestCommands' | Restore diesel generator breaker - from open to close | diesel_breaker | breaker close = 0
0:35 | BANSHEE_SYSTEM/TestCommands' | Trip PV breaker | pv_breaker | breaker open = 1
0:40 | BANSHEE_SYSTEM/TestCommands' | Turn fault 8 on | fault8 | fault 8 on = 1 | does this turn off by itself?
0:40 | BANSHEE_SYSTEM/TestCommands' | Turn fault 8 off | fault8 | fault 8 on = 0
0:45 | BANSHEE_SYSTEM/TestCommands' | Restore PV breaker | pv_breaker | breaker close = 1
0:45 | BANSHEE_SYSTEM/TestCommands' | Request to disconnect from DSO | dso_disconnect | Disconnect port = 1
0:50 | BANSHEE_SYSTEM/TestCommands' | Fault 1 is turned on | fault1 | fault 1 on = 1
0:50 | BANSHEE_SYSTEM/TestCommands' | Fault 1 is turned off | fault1 | fault 1 on = 0
1:10 | BANSHEE_SYSTEM/TestCommands' | Trip diesel generator relay - from close breaker to open breaker | diesel_breaker | breaker open = 1
1:15 | BANSHEE_SYSTEM/TestCommands' | Fault 2 is turned on | fault2 | fault 2 on = 1
1:15 | BANSHEE_SYSTEM/TestCommands' | Fault 2 is turned off | fault2 | fault 2 on = 0
1:20 | BANSHEE_SYSTEM/TestCommands' | Restore diesel generator breaker - from open to close | diesel_breaker | breaker close = 0
1:25 | BANSHEE_SYSTEM/TestCommands' | Connect motor 1 - breaker close | motor1_breaker | breaker close = 0
1:45 | BANSHEE_SYSTEM/TestCommands' | DSO request to reconnect | dso_reconnect | reconnect port = 1
1:45 | BANSHEE_SYSTEM/TestCommands' | DSO request pf command | dso_pf | pf command = 1, pf value = 1.0
1:50 | BANSHEE_SYSTEM/TestCommands' | Trip motor 2 | motor2_breaker | motor 2 breaker open = 1
2:00 | BANSHEE_SYSTEM/TestCommands' | DSO request Q support | dso_q | Q support port = 1, Q support value = xx
2:10 | BANSHEE_SYSTEM/TestCommands' | Fault 4 is turned on | fault4 | fault 4 on = 1
2:10 | BANSHEE_SYSTEM/TestCommands' | Fault 4 is turned off | fault4 | fault 4 on = 0
2:15 | BANSHEE_SYSTEM/TestCommands' | DSO request Demand response | dso_dr | demand response port = 1, DR value = xx
2:20 | BANSHEE_SYSTEM/TestCommands' | Reconnect motor 2 | motor2_breaker | motor 2 breaker close = 0
2:45 | BANSHEE_SYSTEM/TestCommands' | Open POI breaker for feeder 1 | feeder1_breaker | POI breaker open = 1
2:45 | BANSHEE_SYSTEM/TestCommands' | Open POI breaker for feeder 2 | feeder2_breaker | POI breaker open = 1
2:45 | BANSHEE_SYSTEM/TestCommands' | Open POI breaker for feeder 3 | feeder3_breaker | POI breaker open = 1
2:55 | BANSHEE_SYSTEM/TestCommands' | Fault 3 is turned on | fault3 | fault 3 on = 1
2:55 | BANSHEE_SYSTEM/TestCommands' | Fault 3 is turned off | fault3 | fault 3 on = 0
3:00 | BANSHEE_SYSTEM/TestCommands' | Trip motor 1 | motor1_breaker | motor 1 breaker open = 1
3:05 | BANSHEE_SYSTEM/TestCommands' | Fault 5 is turned on | fault5 | fault 5 on = 1
3:05 | BANSHEE_SYSTEM/TestCommands' | Fault 5 is turned off | fault5 | fault 5 on = 0